## pressureDrop
Unit conversion of data sheets logaritmic pressure drop curves
Manufacturer | Viessman
Source data sheets | https://vibooks.viessmann.com/de/de
rho_default in kg/m3 | 995.586 |  | dTTra_nominal | 10
from data sheet
dp=a*x^n
Boiler name | data sheet ID | Q_nom | Q_flow_nominal in W |  | dp in mbar x=V_flow in l/h | dp in mbar x=V_flow in m3/h | dp in Pa x=V_flow in m3/s
|  |  |  | n | a
Vitogas 200-F | 5414039 | 12100 | 11000 | 2.033 | 6.477e-06 |  | 13818640707.8097
|  | 16600 | 15000 | 2.033 | 6.477e-06 |  | 13818640707.8097
|  | 19900 | 18000 | 2.0226 | 5.2271e-06 |  | 9528873688.7936
|  | 24300 | 22000 | 2.0226 | 5.2271e-06 |  | 9528873688.7936
|  | 32000 | 29000 | 1.9265 | 7.6403e-06 |  | 3263576367.8053
|  | 38600 | 35000 | 1.9884 | 3.7095e-06 |  | 4037015758.7956
|  | 46400 | 42000 | 1.9884 | 3.7095e-06 |  | 4037015758.7956
|  | 53000 | 48000 | 1.9986 | 2.616e-06 |  | 3316928443.7118
|  | 66200 | 60000 | 1.9986 | 2.616e-06 |  | 3316928443.7118
| 5811391 | 78300 | 72000 | 2.0089 | 1.8763e-07 |  | 278091798.0072
|  | 91300 | 84000 | 2.0089 | 1.8763e-07 |  | 278091798.0072
|  | 104400 | 96000 | 2.0089 | 1.8763e-07 |  | 278091798.0072
|  | 117400 | 108000 | 2.0089 | 1.8763e-07 |  | 278091798.0072
|  | 130400 | 120000 | 2.0089 | 1.8763e-07 |  | 278091798.0072
|  | 143500 | 132000 | 2.0089 | 1.8763e-07 |  | 278091798.0072
|  | 156500 | 144000 | 2.0089 | 1.8763e-07 |  | 278091798.0072
Vitocrossal 200 | 5368777 | 82000 | 87000 | 2.1371 |  | 0.21296 | 848079468.8325
|  | 108000 | 115000 | 2.1371 |  | 0.21296 | 848079468.8325
|  | 134000 | 142000 | 2.1371 |  | 0.21296 | 848079468.8325
|  | 175000 | 186000 | 1.9067 |  | 0.070318 | 42455811.2401
|  | 232000 | 246000 | 1.9067 |  | 0.070318 | 42455811.2401
|  | 293000 | 311000 | 1.9067 |  | 0.070318 | 42455811.2401

## volume
Volume
Manufacturer | Viessman
Source data sheets | https://vibooks.viessmann.com/de/de
Boiler name | data sheet ID | Q_nom in W | Q_flow_nominal in W | volume in m3
Vitogas 200-F | 5414039 | 12100 | 11000 | 0.0076
|  | 16600 | 15000 | 0.0076
|  | 19900 | 18000 | 0.0097
|  | 24300 | 22000 | 0.0097
|  | 32000 | 29000 | 0.0117
|  | 38600 | 35000 | 0.0138
|  | 46400 | 42000 | 0.0159
|  | 53000 | 48000 | 0.0179
|  | 66200 | 60000 | 0.0219
| 5811391 | 78300 | 72000 | 0.0376
|  | 91300 | 84000 | 0.043
|  | 104400 | 96000 | 0.0483
|  | 117400 | 108000 | 0.0536
|  | 130400 | 120000 | 0.059
|  | 143500 | 132000 | 0.0643
|  | 156500 | 144000 | 0.0696
Vitocrossal 200 (2014) | 5368777 | 82000 | 87000 | 0.229
|  | 108000 | 115000 | 0.225
|  | 134000 | 142000 | 0.221
|  | 175000 | 186000 | 0.306
|  | 232000 | 246000 | 0.292
|  | 293000 | 311000 | 0.279
Vitocrossal 200 (2023) | 5117939 DE | 76000 | 80000 | 0.065
|  | 113000 | 120000 | 0.103
|  | 151000 | 160000 | 0.103
|  | 189000 | 200000 | 0.145
|  | 226000 | 240000 | 0.145
|  | 264000 | 280000 | 0.18
|  | 300000 | 318000 | 0.18